## Start Here
Commercial Lighting Audit Template
Free from LumaQuote · Version October 2026 · Excel and Google Sheets
Record every space and fixture line on site, see energy use and cost as you go, and estimate LED savings, rebates and payback.
HOW TO USE IT
1. Site & Utility | Enter the client, the site and the energy rate from the bill. The rate drives every dollar figure.
2. Spaces | List every room or space before the walk, with a unique name (for example "2F Restroom"), its floor area, ceiling height and schedule. Note existing controls and the controls to add.
3. Fixture Inventory | One line per fixture type per space. Pick the space and the fixture type from the dropdowns, check the wattage on the nameplate, enter the quantity. Hours left blank use the space schedule.
4. Retrofit (optional) | For in-scope lines, enter the LED watts, unit costs and rebate per unit. Savings, cost, net cost and payback calculate on the line.
5. Summary | Totals for the building, by scope and by space, plus the sensors to add. Nothing to type there.
LEGEND
Yellow cells: you type here. Many have a dropdown.
Grey-green cells: calculated. Do not type over them.
Grey italic row: an example of the format. It is never counted in totals.
Pink cell: check it. A measured wattage more than 30% away from the typical value, or a space name not on the Spaces tab.
THE MATH
Existing kWh/yr | Watts used × quantity × hours per day × days per year ÷ 1,000. Watts used is your measured or nameplate value, or the typical system wattage when you leave it blank.
Energy saved | Existing kWh/yr − (LED watts × LED quantity × the same hours ÷ 1,000). Times the energy rate for dollars. Only lines marked "In scope" with LED watts entered.
Simple payback | (Material + labour − rebate) ÷ energy cost saved per year. Demand savings are shown separately and left out of payback, to stay conservative.
Lighting power | Connected watts in the space ÷ floor area (W/sq ft). Handy for code and incentive paperwork.
FIELD TIPS
Hours matter most | Confirm the schedule with the facility manager. One hour a day on a 10-hour schedule is 10% of the energy and of the savings.
System watts, not lamp watts | A 400W metal halide fixture draws about 458W with its ballast. The typical values in this template include the ballast; the nameplate is better.
Count everything | Exit signs, stairwells, mechanical rooms and emergency units go on the inventory too, with a scope status. Out of scope is not the same as not there.
Controls, room by room | Record what controls each space today before suggesting what to add. Where the code asks for it (New York, for example), list the sensors to add with quantities.
Photos | Note photo file names in "Photo refs" so anyone can match a picture to its line later.
WHEN THE SPREADSHEET GETS HEAVY
LumaQuote | The same audit on an iPad, even with no signal, with photos on every line. Back at the desk it becomes a branded PDF or Word proposal with savings, rebates, controls and a 10-year cash flow. Free plan: 3 complete proposals, no credit card.
lumaquote.com/lighting-audit-software
Free to use and share. Typical wattages are starting points; always confirm on site. Savings are estimates, not guarantees.

## Site & Utility
Site & Utility
Fill in before or on arrival. Yellow cells are yours. The energy rate drives every $ figure in the workbook.
| Field | Your audit | Example (format only) | Why it matters
PROJECT
| Client company |  | Lakewood Industrial Supply | Proposal cover and file names.
| Facility name |  | Main distribution center
| Site address |  | 12 Dock Road, Buffalo, NY | Decides the utility and the rebate program.
| Site contact (name, phone, email) |  | Dana Reyes, 555-0142 | Who confirms hours and access.
| Audit date |  | 2026-10-08
| Auditor |  | Sam Patel
| Building type |  | Warehouse / distribution | Context for hours and controls.
| Gross floor area (sq ft) |  | 52000 | Whole building. Space areas go on the Spaces tab.
| Floors / buildings |  | 1 building, 2 floors
UTILITY
| Utility provider |  | National Grid
| Energy rate ($/kWh) |  | 0.13 | From the bill, not an average. All-in rate per kWh.
| Demand rate ($/kW per month) |  | 9.5 | Leave blank if the bill has no demand charge.
| Rebate program |  | Utility lighting incentive | Name and per-fixture amounts go on each line.
| Rebate deadline |  | 2026-12-15
| CO2 factor (kg per kWh) |  | 0.25 | Your grid factor. Used for tonnes of CO2 avoided.
SCOPE
| Controls in scope? |  | Not decided | Ask the client directly. It changes the proposal.
| Budget or payback target |  | Under 4 years
| Proposal due |  | 2026-10-20 | Work back from this date.
| Notes |  | Lift on site. Night shift Mon to Thu.

## Spaces
Spaces
One row per room or space. Give each space a unique name (for example "2F Restroom"): the Fixture Inventory picks it from a dropdown.
SPACE |  |  |  |  | SCHEDULE |  |  | CONDITIONS & EXISTING CONTROLS |  |  | CONTROLS TO ADD |  |  |  | TOTALS FROM THE INVENTORY
Area (floor, wing, building) | Space name (unique) | Space type | Floor area (sq ft) | Ceiling height (ft) | Hours per day | Days per year | Hours per year | Occupancy pattern | Daylight | Existing controls (what is there today) | Add: occupancy sensors (qty) | Add: vacancy sensors (qty) | Add: daylight sensors (qty) | Other controls to add (or "None needed") | Fixture lines | Fixtures (qty) | Connected kW | Existing kWh/yr | Lighting power (W/sq ft) | Notes (access, hazards, lift)
Floor 1 | Example: Warehouse Floor | Warehouse / Distribution | 48000 | 32 | 16 | 260 | 4160 | Intermittent | None | Breaker panel | 12 | 0 | 0 |  | 1 | 64 | 29.312 | 121937.92 | 0.61067 | Scissor lift on site. Aisles 9 to 12 run 24/7 in peak season.
Note on A5: Example row, for format only. It is not counted in the totals. Type your spaces from row 6 down.

## Fixture Inventory
Fixture Inventory
One line per fixture type per space, not per fixture. Hours left blank use the space schedule. The retrofit columns on the right are optional.
IDENTIFY | [5 empty] | EXISTING LOAD | [9 empty] | SITE DETAILS | [7 empty] | RETROFIT AND SAVINGS (OPTIONAL, IN-SCOPE LINES ONLY)
Line # | Space (pick from Spaces) | Area | Fixture type | Lamp designation (F32T8, MH400/U) | Ballast | Typical system W | Measured or nameplate W | Watts used | Qty | Hours/day (blank = space) | Days/yr (blank = space) | Hours per year | Connected kW | Existing kWh/yr | Existing $/yr | Mount height (ft) | Color temp | Control on this line (blank = same as space) | Condition | Scope | Location note (Bay 3, west wall) | Photo refs | Notes | Proposed LED (product or SKU) | LED watts | LED qty (blank = Qty) | Material $ per unit | Labour $ per unit | Rebate $ per unit | Proposed kWh/yr | kWh saved per year | kW reduced | Energy saved $/yr | Project cost $ | Rebate total $ | Net cost $ | Simple payback (yrs)
e.g. | Example: Warehouse Floor | Floor 1 | Metal Halide 400W | MH400/U | Magnetic | 458 | 458 | 458 | 64 |  |  | 4160 | 29.312 | 121937.92 | 15851.9296 | 30 | 4000K |  | Fair | In scope | Aisles 1 to 12 | IMG_0412, IMG_0413 | Lens yellowed on row 3 | UFO high bay 150W, 4000K | 150 |  | 165 | 65 | 40 | 39936 | 82001.92 | 19.712 | 10660.2496 | 14720 | 2560 | 12160 | 1.1407
Note on A5: Example line, for format only. It is not counted in any total. Start your audit on line 1 below.

## Summary
Audit Summary
Calculated from the Spaces and Fixture Inventory tabs. Nothing to type here.
| Client | (not entered)
| Facility | (not entered)
Audit date
| EXISTING LIGHTING |  |  |  | BY SCOPE STATUS |  |  | Energy (kWh/yr)
| Spaces | 0 |  |  | Scope | Lines | Fixtures | Existing | 0
| Fixture lines | 0 |  |  | In scope | 0 | 0 | After retrofit | 0
| Fixtures counted | 0 | All lines, in scope or not. |  | Leave as-is | 0 | 0
| Connected load (kW) | 0 |  |  | Excluded | 0 | 0
| Energy use (kWh/yr) | 0 |  |  | Emergency only | 0 | 0
| Energy cost ($/yr) |  | At the rate on Site & Utility. |  | Already LED | 0 | 0
| Lighting power (W/sq ft) |  | Spaces with a floor area only. |  | Damaged / repair | 0 | 0
[5 empty] | (not set) | 0 | 0
RETROFIT (IN-SCOPE LINES WITH AN LED)
| Fixtures replaced | 0
| Energy saved (kWh/yr) | 0
| Energy saved (%) |  | Of all existing lighting energy.
Energy cost saved ($/yr)
| Demand saved ($/yr) |  | Assumes the lights run at the billing peak. Conservative proposals leave it out.
| Project cost ($) | 0 | Material plus labour per unit only. Add lift, permits and disposal separately.
| Rebates ($) | 0 | Estimate until the program confirms.
| Net cost ($) | 0
| Simple payback (years) |  | Net cost over energy cost saved. Demand savings not included.
| CO2 avoided (tonnes/yr) |  | At the CO2 factor on Site & Utility.
CONTROLS TO ADD (FROM SPACES)
| Occupancy sensors | 0
| Vacancy sensors | 0
| Daylight sensors | 0
| Spaces with other controls noted | 0 | Text in "Other controls to add".
BY SPACE
| Space | Area | Fixtures | Existing kWh/yr | kWh saved/yr | Energy saved $/yr | Sensors to add

## Lists
Lists used by the dropdowns
Add your own fixture types in the yellow rows under the library. They appear in the Fixture Type dropdown and fill the typical wattage.
Fixture type | Group | Typical system W | Space type | Ballast | Condition | Scope | Color temp | Occupancy | Daylight | Existing control (examples) | Yes / No | Building type
T8 4ft 1-Lamp | Fluorescent | 36 | Warehouse / Distribution | Electronic | Good | In scope | 2700K | Always occupied | High | Wall switch | Yes | Warehouse / distribution
T8 4ft 2-Lamp | Fluorescent | 72 | Manufacturing / Production | Magnetic | Fair | Leave as-is | 3000K | Intermittent | Moderate | Dimmer | No | Manufacturing
T8 4ft 3-Lamp | Fluorescent | 108 | Office: Open Plan | Integral / LED driver | Poor | Excluded | 3500K | Rarely occupied | None | Occupancy sensor | Not decided | Office
T8 4ft 4-Lamp | Fluorescent | 144 | Office: Private / Enclosed | None |  | Emergency only | 4000K |  |  | Vacancy sensor |  | Retail
T8 2ft 2-Lamp | Fluorescent | 40 | Retail / Showroom | Unknown |  | Already LED | 5000K |  |  | Daylight sensor |  | School / education
T8 8ft 2-Lamp | Fluorescent | 124 | Classroom / Training |  |  | Damaged / repair | 6500K |  |  | Timer / clock |  | Healthcare
T12 4ft 2-Lamp | Fluorescent | 96 | Corridor / Hallway |  |  |  | Mixed |  |  | Photocell |  | Hospitality
T12 4ft 4-Lamp | Fluorescent | 192 | Restroom / Break Room |  |  |  | Unknown |  |  | BMS / lighting panel |  | Multifamily common areas
T12 8ft 2-Lamp | Fluorescent | 160 | Stairwell | [6 empty] | Breaker panel |  | Parking
T12 2ft 2-Lamp | Fluorescent | 48 | Parking: Indoor | [6 empty] | Always on |  | Mixed use
T5 4ft 2-Lamp | Fluorescent | 62 | Parking: Outdoor | [6 empty] | Unknown |  | Other
T5HO 4ft 2-Lamp | Fluorescent | 116 | Exterior / Grounds
T5HO 4ft 4-Lamp | Fluorescent | 232 | Storage / Mechanical
T5HO 6-Lamp High Bay | Fluorescent | 348 | Lobby / Reception
CFL 13W | CFL | 13 | Conference / Meeting
CFL 23W Spiral | CFL | 23 | Kitchen / Cafeteria
CFL 42W PL | CFL | 42 | Gym / Recreation
CFL Downlight 6" | CFL | 26 | Other
Incandescent 60W | Incandescent | 60
Incandescent 100W | Incandescent | 100
Halogen MR16 50W | Halogen | 50
Halogen PAR30 75W | Halogen | 75
Halogen PAR38 90W | Halogen | 90
Halogen Downlight 75W | Halogen | 75
Metal Halide 70W | Metal Halide | 95
Metal Halide 100W | Metal Halide | 128
Metal Halide 150W | Metal Halide | 185
Metal Halide 175W | Metal Halide | 210
Metal Halide 250W | Metal Halide | 290
Metal Halide 400W | Metal Halide | 458
Metal Halide 1000W | Metal Halide | 1100
HPS 70W | HPS | 95
HPS 100W | HPS | 128
HPS 150W | HPS | 185
HPS 250W | HPS | 295
HPS 400W | HPS | 465
Vapor Tight 4ft 2-Lamp | Special | 72
Wall Pack HPS 70W | Special | 95
Shoebox 250W HPS | Special | 295
Shoebox 400W HPS | Special | 465
Flood MH 400W | Special | 458
Flood MH 1000W | Special | 1100
Recessed Can BR30 | Special | 65
Recessed Can BR40 | Special | 85
Exit Sign (Incandescent) | Special | 40
Typical system watts include the ballast (a 400W metal halide draws about 458W). They are starting points: always confirm on the nameplate or with a meter.
Note on A50: Your own fixture types go here: name, group and typical system watts (lamp plus ballast).